## REQUIREMENT-A(REPLACE)
Attachment 2
CUI/FEDCON
REQUIREMENT-A
ITEM NO. | APPLICABLE STANDARDS | DISCRIPTION
1 | ASME A17.1-2.1.1.1(IBC-2015 - 713) | 2-hour fire resistant hoistway construction. | MANUFACTURERS | OTIS | OTIS | SCHINDLER | SCHINDLER | SCHINDLER | HITACHI | HITACHI | HITACHI | SCHINDLER | SCHINDLER
2 | ASME A17.1-2.1.1.1.3 (IBC-2015 - 716) | Minimum 1 ½ -hour fire rating for hoistway entrance assemblies. | BLDG.NO | 1529 | 1530 | 239 | 239 | 430 | 405 | 580 | 580 | 5114 | 5114
3 | ASME A17.1-2.1.4 | Control of Smoke and Hot Gases in the Hoistway | ELEVATOR ID | EL-M15 | EL-M17 | EL-M29 | EL-M30 | EL-M36 | EL-M44 | EL-M45 | EL-M46 | EL-H9 | EL-H10
4 | ASME A17.1-2.1.6 | 75 degree bevels on all projections and recesses into the hoistway greater than 100 mm (4 in.) on all sides not used for loading or unloading.
5 | ASME A17.1-2.2.2.5 | Sump pump and drain system for phase II Firefighters’ operation in the pit. (min. 11.4 m3/h / 3,000 gal/h)
6 | ASME A17.1-2.2.4 | Pit ladder. (400 mm W) x (300 mm S) x (1200 mm H, above the sill of the access landing.)
7 | ASME A17.1-2.2.5 | Permanent guarded light in the pit. (Not less than 100 lx at the pit floor) Locate pit light switch same side of pit access ladder, mounted at accessible height from landing access.
8 | ASME A17.1-2.2.6 | Stop switch (Push/Pull type) in the pit. Locate Push/Pull type Stop Switch approx. 450 mm height measured from access landing, same side as pit ladder.
9 | ASME A17.1-2.3.2 | Counterweight guard in the pit.
10 | ASME A17.1-2.4.1 | Bottom car clearances in the pit. * Refuge space: (600 x 1200 x 600 H) mm or (450 x 900 x 1070 H) mm
11 | ASME A17.1-2.4.7 | Top of car clearances. * Refuge space: 0.5 m2 (Not less than 600 mm on any side) and 1100 mm H
12 | ASME A17.1-2.5 | Horizontal car and counterweight clearances and fascia plate.
13 | ASME A17.1-2.7.1.1 (IBC-2015 - 3006.4) | 2-hour fire resistant construction for elevator machine room.
14 | ASME A17.1-2.7.1.1.2 (IBC-2015 - 716) | Minimum 1 ½ -hour fire rating for machine room door.
15 | ASME A17.1-2.7.9.1 | Lighting of the machine room. (Not less than 200 lx at the floor level)
16 | ASME A17.1-2.7.9.2 | Ventilation for elevator machine room.
17 | ASME A17.1-2.8.2 (NFPA70-2017 - 620.11A) | Hoistway door interlock wires with fire rated type. (Not less than 200℃)
18 | ASME A17.1-2.8.2 (NFPA70-2017 - 620.21) | Electrical wiring. (Hoistways and Pits, Cars and Machine Rooms)
19 | ASME A17.1-2.8.2(NFPA70-2017 - 620.85) | Duplex receptacles of the machine room, car top and pit with Ground Fault Circuit Interrupter (GFCI) type.
20 | ASME A17.1-2.8.3.3.2(NFPA72-2016 - 21.4) | When sprinklers are installed in the machine room or hoistway, provide shunt trip means (automatically disconnect) for the main line power supply.
21 | ASME A17.1-2.10 | Guarding for moving equipment in machine room.
22 | ASME A17.1-2.11.3 | Door closers to hoistway doors of horizontal slide type.
23 | ASME A17.1-2.11.10.2 | Illumination at landing sills. (Not less than 100 lx)
24 | ASME A17.1-2.11.11.6 | Bottom guides to hoistway doors of horizontal slide type.
25 | ASME A17.1-2.11.11.8 | Safety retainers to hoistway doors of horizontal slide type.
26 | ASME A17.1-2.12.7 | Hoistway access switch.
27 | ASME A17.1-2.13.4.2.3 | Door closing force of the car. (Not exceed 135N / 30 lbs)
28 | ASME A17.1-2.14.1.5 | Emergency exit with hinge in the top of the car.
29 | ASME A17.1-2.14.1.7 | Handrail of the standard railing on top of car.
30 | ASME A17.1-2.14.2.3 | Ventilation for car enclosure.
31 | ASME A17.1-2.14.5.7 | Restricted opening of hoistway or car doors for passenger elevators. When a car is outside the unlocking zone, door opening not to exceed 100 mm (4”) from inside the car and when the car is within the unlocking zone, doors shall be openable from within the car.
32 | ASME A17.1-2.14.7.1.1 and 2.14.7.1.2 | Lighting fixture of the car. (Not less than two lamps or sets of lamps.) (Passenger: Not less than 50 lx), (Freight: Not less than 25 lx)
33 | ASME A17.1-2.14.7.1.3 | Emergency light (two lamps) of the car. (Not less than 2 lx)
34 | ASME A17.1-2.14.7.1.4 | Lighting on the car top. (Not less than 100 lx)
35 | ASME A17.1-2.15.9 | Platform Guards (Aprons) 1220 mm H (48 in.)
36 | ASME A17.1-2.16.3 and 2.20.2.1 and 2.20.2.2 and 2.18.5.3 | Crosshead data plate. Rope data tag to the fastening. (For suspension rope and governor rope.)
37 | ASME A17.1-2.16.5.1 | Sign for freight elevator in the car enclosure.
38 | ASME A17.1-2.19 | Emergency brake for Ascending car over speed and Unintended car movement protection. (The emergency brake shall be designed to decelerate the car be acting directly on the elevator hoist ropes.)
39 | ASME A17.1-2.22.3 and 2.22.4 | Buffer marking plate.
40 | ASME A17.1-2.26.12 and ADAAG-4.10 | Means (Braille, Voice, etc.) for handicap. Mirror material is not glass but stainless metal with non-sharp beveled edges.
41 | ASME A17.1-2.27.1.1 2.27.1.1.6 | Two way communication means between the car and a location staffed by authorized personnel include a means to verify operability of the telephone line. (Provide protection feature to prevent accidental depressing of this button.)
42 | ASME A17.1-2.27.2 2.27.2.3 | Standby power system and operation. An illuminated signal(s) marked “ELEVATOR EMERGENCY POWER” shall be provided in the elevator lobby at the designated level.
43 | ASME A17.1-2.27.3.1 | Phase I emergency recall operation by key switch.
44 | ASME A17.1-2.27.3.2 (NFPA72-2016 - 21.3) | Phase I emergency recall operation by fire alarm initiating devices
45 | ASME A17.1-2.27.3.3 | Phase II firefighters’ emergency in-car operation.
46 | ASME A17.1-2.27.3.4 | The failure and subsequent restoration of electrical power (normal, emergency, or standby) shall not cause any elevator to be removed from Phase I Emergency Operation or Phase II Emergency In-Car Operation.
47 | ASME A17.1-2.27.5 | Firefighters’ Emergency Operation: Automatic Elevators With Designated- Attendant Operation.
48 | ASME A17.1-2.27.6 | Inspection operation or hoistway access operation shall take precedence over Phase I Emergency Recall Operation.
49 | ASME A17.1-2.27.7 | Instructions for operation of elevators under Phase I Emergency Recall Operation and Phase II Emergency In-Car Operation.
50 | ASME A17.1-8.4.3 | Jump guards of earthquake for suspension members.
51 | ASME A17.1-8.4.10.1 | Earthquake sensors (primary and secondary waves) and counterweight displacement switch for earthquake emergency operation. (Car Speed ≥ 0.75 m/s and Seismic risk zone 3 or greater)
52 | ASME A17.1-8.6.1.6.5 | Fire extinguisher for elevator machine room.
53 | ASME A17.1-8.9 | Code data plate on the control panel in the machine room.
54 | ASME A17.1-2019 2.27.1.1.3(K) | A means to display video to observe passengers at any location on the car floor, to authorized personnel for entrapment assessment, shall be provided.
55 | UFC3-490-06 (6-2.1) | Lighting fixture in the hoistway. (Minimum of every 10 feet (3 m) vertically up the hoistway.)
56 |  | Cabinet for storage of O&M documentation and wiring diagrams in the machine room. Minimum size: (508 mm W) x (305 mm D) x (762 mm H)
57 |  | Infra-red Car Door Protection.An Infra-red Curtain Unit (ICU), with a minimum of 150 beams, must be used to protect the full height and width of the car door opening.
58 |  | REMOVE EXST RADIO FIRE ALARM PANEL
59 |  | PROVIDE RADIO FIRE ALARM ADDRESSABLE PANEL
60 |  | PROVIDE/MODIFY NEW WINDOW ON EXST FIRE ALARM PANEL FOR ELEVATOR EMERGENCY OPERATION
61 |  | PROVIDE MCCB IN EXST PANELBOARD FOR SUMP PUMP
62 |  | PROVIDE ELEC POWER FEEDER SYSTEM FOR SUMP PUMP
63 |  | MODIFY NEW WINDOW ON EXST RADIO FIRE ALARM PANEL FOR SHUNT TRIP CIRCUIT FOR ELEVATOR.
64 |  | PROVIDE MCCB IN EXST PANELBOARD FOR SURVEILLANCE CAMERA
65 |  | PROVIDE ELEC POWER FEEDER SYSTEM FOR SURVEILLANCE CAMERA
66 |  | PROVIDE MCCB IN EXST PANELBOARD FOR LIGHT IN ELEVATOR PIT
67 |  | PROVIDE ELEC POWER FEEDER SYSTEM FOR LIGHT IN ELEVATOR PIT
68 |  | PROVIDE TWO-WAY COMMUNICATION SYSTEM FOR ELEVATOR

## REQUIREMENT-B(REPAIR)
Attachment 2
CUI/FEDCON
ITEM NO. | APPLICABLE STANDARDS | DISCRIPTION | MANUFACTURERS | OTIS | DAIKO | OTIS | OTIS | OTIS | OTIS |  | OTIS | OTIS |  | OTIS | DAIKO | OTIS | DAIKO |  | DAIKO |  | OTIS |  | OTIS | OTIS |  | OTIS | OTIS | OTIS | OTIS | OTIS |  | DAIKO |  | SANSEI-YUSO |  | OTIS | MORIYA
|  |  | BLDG.NO | 16 | 35 | 98 | 100 | 132 | 151 |  | 155 | 200 |  | 203 | 311 | 442 | 480 |  | 487 |  | 1512 |  | 1529 | 1649 |  | 1651 | 1653 | 1665 | 2001 | 5028 |  | 5035 |  | 5039 |  | 5118 | 6056
|  |  | ELEVATOR ID | EL-M1 | ELM-57 | EL-M31 | EL-M2 | EL-M39 | EL-M25 | EL-M26 | EL-M24 | EL-M4 | EL-M5 | EL-M6 | EL-M49 | EL-M23 | EL-M55 | EL-M56 | EL-M50 | EL-M51 | EL-M47 | EL-M48 | EL-M16 | EL-M18 | EL-M19 | EL-M20 | EL-M21 | EL-M22 | EL-M53 | EL-H14 | EL-H15 | EL-H16 | EL-H17 | EL-H12 | EL-H13 | EL-H20 | EL-M52
1 | ASME A17.1-2.1.6 | Provide bevel (75 degree) to the projections, recesses, and setbacks in the hoistway. |  |  |  |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 |  |  |  | 〇 | 〇 | 〇 | [8 empty] | 〇 |  | 〇
2 | ASME A17.1-2.2.2.5 | Provide sump pump and drain system for phase Ⅱ firefighters operation in the pit. |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇
3 | ASME A17.1-2.2.4 | Provide proper pit ladder in the pit. |  |  |  |  | 〇 |  | 〇 | 〇 |  | 〇 | 〇 | [14 empty] | 〇 | [8 empty] | 〇
4 | ASME A17.1-2.2.4 | Provide skid proof means to cleats of pit access ladder. | [26 empty] | 〇
5 | ASME A17.1-2.2.5 | Provide permanent light in the pit. | [16 empty] | 〇 | 〇 | [13 empty] | 〇 | 〇 |  | 〇
6 | ASME A17.1-2.2.5 | Relocate pit light switch adjacent to upper pit stop switch approx. 450 mm above landing level of 1st floor. | [16 empty] | 〇 | 〇 | [8 empty] | 〇 | [7 empty] | 〇
7 | ASME A17.1-2.2.5 | Provide appropriate illumination, 100 lx (10fc) at pit floor. | [16 empty] | 〇 | 〇 | [8 empty] | 〇 | [7 empty] | 〇
8 | ASME A17.1-2.2.6 | Replace pit stop switch with new push-to-stop type. | [31 empty] | 〇 | 〇
9 | ASME A17.1-2.2.6 | Relocate the pit stop switch to the pit ladder side |  |  | 〇
10 | ASME A17.1-2.3.2 | Provide counterweight guard in the pit.(Exception: When compensating chains/ropes are installed.) | [10 empty] | 〇 | 〇 |  | 〇 |  |  | 〇 | 〇 | [6 empty] | 〇 | 〇 | [5 empty] | 〇 | 〇 |  | 〇
11 | ASME A17.1-2.4.2 ASME A17.1-8.6.3.12, 8.6.5.10 | Repair (shorten) the suspension ropes to ensure proper clearance (runby) between the counterweight and the counterweight buffer. | [12 empty] | 〇
12 | ASME A17.1-2.4.5 | Provide counterweight runby data plate and locate conspicuously on counterweight guard. |  |  | 〇 |  |  | 〇
13 | ASME A17.1-2.5.1.5.1 | Provide fascia plate to the hoistway enclosure in accordance ASME A17.1 - 2.5.1.5. Existing one, The hoistway door is horizontal sliding door. The clearance between the edge of the car platform sill and the hoistway enclosure is 235mm. | [12 empty] | 〇
14 | ASME A17.1-2.7.6.3.2 (c) | Provide proper lighting fixture at the elevator machine room. ASME A17.1-2016 Section 2.7.6.3.2 (c) is required at least 200 lx (19 fc) lighting fixture at the floor level. | [26 empty] | 〇
15 | ASME A17.1-2.8.2 | Replace hoistway door interlock wires with fire rated type ones. (NFPA70 - 620.11 A) | [9 empty] | 〇 | 〇 | 〇 |  | 〇 |  |  | 〇 | 〇 | [6 empty] | 〇 | [6 empty] | 〇 | 〇 |  | 〇
16 | ASME A17.1-2.8.2 | Replace receptacles of the car top and pit with GFCI type ones. (NFPA70 - 620.85) | [11 empty] | 〇 |  | 〇 |  |  | 〇 | 〇 | [6 empty] | 〇 | 〇 | [5 empty] | 〇 |  |  | 〇
17 | ASME A17.1-2.8.3.3.2 | Provide shunt trip device to disconnect main power supply automatically when the sprinkler is activated in the machine room or hostway. (Urgent) | [8 empty] | 〇 | 〇 | 〇 |  |  | 〇 | [10 empty] | 〇 | 〇
18 | ASME A17.1-2.8.3.3.2 | Provide flow switch for shunt trip system to the sprinkler piping. | [31 empty] | 〇
19 | ASME A17.1-2.8.3.3.2 | Provide flow switch for shunt trip system to the sprinkler piping in accordance with ASME A17.1-2.8.3.3.2 and NFPA 72-21.4. (Urgent) Curently, there is no device to active the shunt trip. | [16 empty] | 〇 | 〇
20 | ASME A17.1-2.1 | Provide proper guarding for moving equipments in machine room. | [16 empty] | 〇 | 〇 | [13 empty] | 〇 | 〇 |  | 〇
21 | ASME A17.1-2.10.2.3 | Provide toe-board to standard railing (Handrail) on the top of the car. ASME A17.1-2.10.2.3 Toe-Board. The toe-board shall be securely fastened and have a height not less than 100 mm (4 in.) above the working surface. | [5 empty] | 〇
22 | ASME A17.1-2.11 | Repair bent door panel of the elevator hoistway at the second floor. | [13 empty] | 〇
23 | ASME A17.1-2.11.11.8 | Provide safety retainers to hoistway doors of horizontal slide type. |  | 〇 |  | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | [5 empty] | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  |  |  | 〇 | 〇 | 〇 | 〇
24 | ASME A17.1-2.13.4.2.3 | Repair and adjust door closing force (Not exceed 135N / 30 lbs). | [31 empty] | 〇
25 | ASME A17.1-2.13.5.2 | Provide proper reopening device to the center-opening car doors. Currently, the reopening device has been installed only on one side of the car doors. It’s should be installed on both car doors or provide multiple type infrared door reopening device. |  |  |  | 〇 |  |  | 〇 | 〇 |  | 〇
26 | ASME A17.1-2.14.1.5 | Provide stop switch and hinge or chain to the emergency exit cover of the top of the car. | [31 empty] | 〇 | 〇
27 | ASME A17.1-2.14.1.5.1(f) | Provides electrical device to the hoistway smoke detector inspection hatch for prevent elevator car operation when the inspection hatch is opening. | [5 empty] | 〇
28 | ASME A17.1-2.14.1.7 | Provide proper standard railing (Handrail) on the top of the car. |  | 〇 |  | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | [7 empty] | 〇 | 〇 | 〇 | 〇 | 〇 | [5 empty] | 〇 | 〇
29 | ASME A17.1-2.14.5.7 | Provide restricted opening of hoistway or car doors for passenger elevators. |  | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | [6 empty] | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 |  |  |  | 〇 | 〇 | 〇 | 〇
30 | ASME A17.1-2.14.7.1.4 | Provide permanent illumination. It shall be 100lx (10fc) at working surface of top car. | [26 empty] | 〇
31 | ASME A17.1-2.15.9 | Provide proper car platform guard (Aprons) to under of the car. | [34 empty] | 〇
32 | ASME A17.1-2.16.3 | Provide crosshead data plate on the top of the car. | [10 empty] | 〇 | 〇 | 〇 | [12 empty] | 〇 | [5 empty] | 〇 | 〇 |  | 〇
33 | ASME A17.1-2.16.5.1 | Provide a sign for freight elevator in the car. (Freight Class: C2) | [34 empty] | 〇
34 | ASME A17.1-2.17 | Replace improper car safety devises (Type A) with new ones. (It will be replaced by current construction.) Also provide manufacturer certificate of the car safety devises in accordance with JIS A 4305: 2016. | [16 empty] | 〇 | 〇
35 | ASME A17.1-2.18.5.3 | Provide rope data tag to the suspension rope fastening and the governor rope fastening. | [34 empty] | 〇
36 | ASME A17.1-2.20.2 | Provide crosshead data plate on the top of the car. | [10 empty] | 〇 | 〇 | 〇 | [12 empty] | 〇 | [5 empty] | 〇 | 〇 |  | 〇
37 | ASME A17.1-2.20.2.2 | Provide rope data tag to the suspension rope fastening and the governor rope fastening. | [34 empty] | 〇
38 | ASME A17.1-2.22.3 | Provide buffer marking plates for the car buffer and counterweight buffer. | [34 empty] | 〇
39 | ASME A17.1-2.22.4 | Provide buffer marking plates for the car buffer and counterweight buffer. | [34 empty] | 〇
40 | ASME A17.1-2.26.12 | Provide proper means (Braille, Voice, etc.) in accordance with Accessible and Usable Buildings and Facilities (ICC A117.1). |  | 〇 |  |  | 〇 |  |  |  | 〇 |  | 〇 | [10 empty] | 〇 |  |  |  | 〇
41 | ASME A17.1-2.27.1.1 | Provide two way communication means between car and fire station (RDC). (Urgent) Currently the existing call system can be communicated only between the car and the office. It shall be connected to 24 hours staffed office. | [34 empty] | 〇
42 | ASME A17.1-2.27.1.1.6 | Provide verify operability means of the telephone line to the two way communication device. | [26 empty] | 〇
43 | ASME A17.1-2.27.2 | Provide standby power operation system. | [24 empty] | 〇 | 〇
44 | ASME A17.1-2.27.2 | Provide stanby power operation system and batteries | [24 empty] | 〇 | 〇
45 | ASME A17.1-2.27.3.1 | Provide Phase Ⅰ emergency recall operation by key switch. | [9 empty] | 〇 | 〇 | 〇 | [12 empty] | 〇 | [6 empty] | 〇 | 〇 |  | 〇
46 | ASME A17.1-2.27.3.1.6 | Correct improper combination operation between emergency stop switch in the car and Phase I emergency recall operation. Currently, when turn on the emergency stop switch in the car during Phase I emergency recall operation before the door closes completely, the car door was stopped. After that, even after the emergency stop switch is returned to RUN and the car door was completely closed, the car was not recalled and the operator was trapped in the car. | [34 empty] | 〇
47 | ASME A17.1-2.27.3.1.6 (g) | Correct improper door open function for the vertically sliding doors at the elevator lobby during Phase I Emergency Recall Operation. It’s shall be correct in accordance with ASME A17.1 - 2.27.3.1.6 (g). (It will be repaired by current contract.) ASME A17.1 - 2.27.3.1.6 (g) Where provided on elevators with vertically sliding doors, corridor door open and door close buttons shall remain operative. | [16 empty] | 〇 | 〇
48 | ASME A17.1-2.27.3.1.6 (k) | Correct improper reset function of Phase I emergency recall operation in accordance with ASME A17.1 –2.27.3.1.6 (k). | [34 empty] | 〇
49 | ASME A17.1-2.27.3.2 | Provide Phase Ⅰ emergency recall operation by fire alarm initiating devices. | [9 empty] | 〇 | 〇 | 〇 | [12 empty] | 〇 | 〇 | [5 empty] | 〇 | 〇
50 | ASME A17.1-2.27.3.2 | Provide smoke detector in the machine room for the fire recall. (NFPA72 - 21.3) | [9 empty] | 〇 | 〇 | 〇 | [12 empty] | 〇 | 〇
51 | ASME A17.1-2.27.3.2 | Provide smoke detector at each elevator lobby for the fire recall. (NFPA72 - 21.3) | [9 empty] | 〇 | 〇 | 〇 | [12 empty] | 〇
52 | ASME A17.1-2.27.3.2 | Correct improper Phase I emergency recall operation system. When the smoke detector at the roof floor (elevator lobby) is activated, the Phase I emergency recall operation by fire alarm initiating devices does not work. | [18 empty] | 〇 | 〇
53 | ASME A17.1-2.27.3.2 | Correct improper Phase Ⅰemergency recall operation by fire alarm initiating devices in accordance with ASME A17.1-2.27.3.2. (Position indicator, Phase Ⅱwas not activated, etc.) | [34 empty] | 〇
54 | ASME A17.1-2.27.3.2.1 | Smoke detectors shall not be installed in unsprinklered elevator hoistways unless they are installed to activate the elevator hoistway smoke relief equipment. | [13 empty] | 〇
55 | ASME A17.1-2.27.3.3 | Provide Phase Ⅱ firefighters’ emergency in-car operation. | [9 empty] | 〇 | 〇 | 〇 |  | 〇 | [10 empty] | 〇 | 〇 | [5 empty] | 〇 | 〇
56 | ASME A17.1-2.27.3.3 | Repair improper phase Ⅱoperation in accordance with ASME A17.1-Section 8.4.10.1.3. When the seismic switch has been activated, the car should be operated by Phase ⅡEmergency In-Car Operation. (Important) | [25 empty] | 〇
57 | ASME A17.1-2.27.3.3 | Repair inactive door shoe of the car while Phase Ⅰemergency operation | [25 empty] | 〇
58 | ASME A17.1-2.27.3.3 | Repair incorrect phase Ⅱfirefighters' operation after reset with key |  |  |  | 〇 |  |  | 〇 | 〇
59 | ASME A17.1-2.27.3.3 | Correct improper Phase Ⅱfirefighters' emergency in-car operation in accordance with ASME A17.1-2.27.3.3. (Door open and close function, HOLD function, OFF function.) | [34 empty] | 〇
60 | ASME A17.1-2.27.6 | Correct improper combination operation between inspection operation and Phase I fire recall operation in accordance with ASME A17.1 - 2.27.6. When the Phase I fire recall operation is activated while inspection operation, the car shall be remain until removed inspection operation. The audible signals and visual signals shall be activated in the car to alert the operator of an emergency. | [5 empty] | 〇 | [10 empty] | 〇 | 〇
61 | ASME A17.1-8.4.3 | Provide proper jump guards of earthquake for suspension ropes and governor rope. (For Main sheave, Deflector sheave, Governor and Governor tension sheave) | [9 empty] | 〇 | 〇 | 〇 |  | 〇 | [10 empty] | 〇 | 〇 | [5 empty] | 〇
62 | ASME A17.1-8.4.10.1.3 | Repair improper phase II operation in accordance ASME A17.1 - Section 8.4.10.1.3. When the seismic switch has been activated, the car should be operated by Phase II Emergency In-Car Operation. (Important) | [25 empty] | 〇
63 | ASME A17.1-8.6.1.6.5 | Provide fire extinguisher in the elevator machine room. | [31 empty] | 〇
64 | ASME A17.1-8.6.3.12 | Repair (shorten) the suspension ropes to ensure proper clearance (runby) between the counterweight and the counterweight buffer. | [12 empty] | 〇
65 | ASME A17.1-8.6.5.10 | Repair (shorten) the suspension ropes to ensure proper clearance (runby) between the counterweight and the counterweight buffer. | [12 empty] | 〇
66 | ASME A17.1-8.9 | Provide code data plate on the control panel. | [34 empty] | 〇
67 | NFPA72 21.3.6 | Recommendation:Remove unnecessary smoke detector in the hoistway in accordance with NFPA72 (21.3.6). Because, sprinkler does not exist in the hoistway. NFPA72 (21.3.6) Smoke detectors shall not be installed in unsprinklered elevator hoistways unless they are installed to activate the elevator hoistway smoke relief equipment. | [13 empty] | 〇
68 | NFPA72-21.4.4* | Provide proper shunt trip monitor system in accordance with NFPA72- 21.4.4*. | [26 empty] | 〇 |  |  | 〇 | 〇
69 | UFGS-14 21 23(1.3.3 ~ 1.3.5) | Provide metal cabinet, wiring diagrams and maintenance manuals in the pit for MRL elevator. Cabinet size: minimum (508 mm W) x (305 mm D) x (762 mm H) |  |  | 〇 | [31 empty] | 〇
70 | UFGS-14 21 23 (1.3.3, 1.3.4 and 1.3.5) | Provide metal cabinet for storage for O&M documentation and wiring diagrams in the machine room. Minimum size: (508 mm W) x (305 mm D) x (762 mm H) | [14 empty] | 〇 | 〇 | [10 empty] | 〇
71 | Correct improper alarms for 100% load and 150% load of the weight sensor. The alarm single shall be clearly difference between both alarm sounds. | [35 empty] | 〇
72 | Correct improper clearance between governor rope and concrete wall. | [27 empty] | 〇
73 | Provide crosshead data plate on the top of the car. | [14 empty] | 〇 | [10 empty] | 〇
74 | Provide drain pan under the AC unit in the machine room to prevent condensation from falling onto the control panel. | [27 empty] | 〇
75 | Provide vent hood and filter on the louvers in the machine room to prevent rain and dust from entering the machine room. | [27 empty] | 〇
76 | Replace broken up select buttons at the 1st floor elevator lobby and 2nd floor lobby with new ones. (Function is OK.) | [32 empty] | 〇
77 | Replace broken 1st floor and 4th floor select buttons and open button in the car with new ones. (Function is OK) | [32 empty] | 〇
78 | This elevator has been shut down due to broken emergency brake (rope gripper) since Dec 2021. | [19 empty] | 〇
79 | This elevator has been restricted to use for "Material Lift and No passenger/No Riders" due to improper car safety devices. (Disable in car floor calls until this defect is corrected.) | [17 empty] | 〇 | 〇
80 | This elevator has been restricted to use for "Material Lift and No passenger/No Riders" as the defects has not been fixed. | [14 empty] | 〇
81 | REMOVE EXST RADIO FIRE ALARM PANEL | [10 empty] | 〇 | 〇 | 〇 |  | 〇 | [10 empty] | 〇 | [6 empty] | 〇 | 〇
82 | PROVIDE RADIO FIRE ALARM ADDRESSABLE PANEL | [10 empty] | 〇 | 〇 | 〇 |  | 〇 | [10 empty] | 〇 | 〇 | [5 empty] | 〇 | 〇
83 | PROVIDE/MODIFY NEW WINDOW ON EXST FIRE ALARM PANEL FOR ELEVATOR EMERGENCY OPERATION | [9 empty] | 〇 | 〇 | 〇 | 〇 |  | 〇 | [10 empty] | 〇 | 〇 | [5 empty] | 〇 | 〇
84 | PROVIDE MCCB IN EXST PANELBOARD FOR SUMP PUMP |  |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇
85 | PROVIDE ELEC POWER FEEDER SYSTEM FOR SUMP PUMP |  |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇
86 | MODIFY NEW WINDOW ON EXST RADIO FIRE ALARM PANEL FOR SHUNT TRIP CIRCUIT FOR ELEVATOR. | [9 empty] | 〇 | [7 empty] | 〇 | 〇 | [8 empty] | 〇 |  |  | 〇 | 〇
87 | MODIFY NEW WINDOW ON EXST RADIO FIRE ALARM PANEL FOR ELECTRICAL DEVICE OF HOISTWAY SMOKE DETECTOR INSPECTION HATCH. | [6 empty] | 〇
88 | PROVIDE MCCB IN EXST PANELBOARD FOR LIGHT IN ELEVATOR PIT | [17 empty] | 〇 | 〇 |  |  | 〇 | [10 empty] | 〇 | 〇 |  | 〇
89 | PROVIDE ELEC POWER FEEDER SYSTEM FOR LIGHT IN ELEVATOR PIT | [17 empty] | 〇 | 〇 |  |  | 〇 | [10 empty] | 〇 | 〇 |  | 〇
90 | REMOVE EXST INTERPHONE SYSTEM FOR ELEVATOR | [35 empty] | 〇

## REQUIREMENT-C(ALOIM-2000)
Attachment 2
CUI/FEDCON
REQUIREMENT-C
ITEM NO. | APPLICABLE STANDARDS | DISCRIPTION | MANUFACTURERS | BANZAI | BANZAI | BANZAI | BANZAI | NISSALCO | NISSALCO | NISSALCO | NISSALCO | NISSALCO | NISSALCO | NISSALCO | BEND PAK
|  |  | BLDG.NO | 203 | 203 | 203 | 203 | 1601 | 1601 | 1625 | 1625 | 1625 | 1625 | 1625 | 203
|  |  | AL ID | AL-S1 | AL-S2 | AL-S3 | AL-S4 | AL-S5 | AL-S6 | AL-S7 | AL-S8 | AL-S9 | AL-S10 | AL-S11 | AL-S12
1 | ALOIM-2000-1.6 | Replace deteriorated concrete floor foundation for automotive lift with new one. Currently the floor foundation is cracked. Also, some anchor bolts cannot be tightened. MANUFACTURER INSTALLATION AND OPERATION MANUAL (Bend Pak): If anchor bolts do not hold when torqued to required amount, concrete must be replaced. Saw cut and remove 24” x 24” square area under each column base then re-pour with reinforced 2500 PSI concrete to a depth of six inches minimum, keying new concrete under existing floor. | [12 empty] | 〇
2 | ALOIM-3.2 | Replace deteriorated pneumatic solenoid valve with new one | [10 empty] | 〇
3 | ALOIM-5.6.2.1-4,5.6.2.6 | The caution sign plate shall be indicated in Japanese and English. (manufacture name, date, maximum capacity, power source, caution plate, and manual) | [5 empty] | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇
4 | ALOIM-5.6.2.7 | Safety color cording for working area is not indicated properly. (Yellow tape) |  |  | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 | 〇 |  | 〇 | 〇
5 | ALOIM-5.6.2.8 | Repair damaged and cracked concrete floor around the automotive lift. |  | 〇
6 | ALOIM-5.6.2.16 | Safety locking device is not installed. | [5 empty] | 〇 | 〇 | 〇 | 〇
7 | ALOIM-5.6.3.1 | Replace existing automotive lift with new one as the most of parts are getting deteriorated. And additional safety locking device should be adapted. Currently, oil leakage has been stopped. This automotive lift has been operating since 1991. All the systems are getting worse due to long term used. | [6 empty] | 〇
8 | ALOIM-5.6.3.3 | [7 empty] | 〇
9 | ALOIM-5.6.6.2 | [7 empty] | 〇
10 | ALOIM-5.6.3.5 | Repair deteriorated pit cover for automotive lift. | [7 empty] | 〇 | 〇
11 |  | Remove unused plunger, hydraulic oil tank and associated piping for the automotive lift. This automotive lift is not in used due to customer request and has been removed swing arms on MAR 2019. However, there are still existing plungers, hydraulic oil tanks, and related plumbing in the underground. | [9 empty] | 〇

## REQUIREMENT-D(ASME B20.1)
Attachment 2
CUI/FEDCON
ITEM NO. | APPLICABLE STANDARDS | DISCRIPTION | MANUFACTURERS | WATABE SANGYO | WATABE SANGYO | SUZUKI SEIKI | AIWA
|  |  | BLDG.NO | 130 | 132 | 303 | 319
|  |  | VRC ID | VRC-M42 | VRC-M43 | VRC-M37 | VRC-M41
1 | ASME B20.1 | Repair bent openwork gate for the car door. (It will be repaired by current contract.) |  |  |  | 〇
2 | ASME B20.1-5.9.2 | To prevent fire and spread fire, enclose the hoistway with a metal plate and install a fire door in front of the car door |  | 〇 | 〇 |  | 〇